## Sheet1
Luminaire list (Building 1, Storey 1)
Index | Manufacturer | Article name | Fitting | Luminous flux | Maintenance factor | Connected load | Quantity
1 | Philips | DN570B 1 xLED12S/830 C | 1x LED12S/830 | 1300 lm | 0.8 | 9.9 W | 222
4 | Philips | SM341C PSD-T L1500 ACL 1 x26S/940 MLO | 1x 26S/940 | 2600 lm | 0.8 | 24.5 W | 29
5 | Philips | DN470B PSD-VLC-E P 1 xLED30S/840 C P | 1x LED30S/840 | 3200 lm | 0.8 | 23 W | 214
6 | Philips | SM340C PSD L1500 SI 1 x52S/940 PCS | 1x 52S/940 | 5200 lm | 0.8 | 39 W | 9
SIR | Name | Parameter | Min | Max | Average | Min/average | Min/max
1 | Calculation surface 1 | Perpendicular illuminance | 159 lx | 256 lx | 215 lx | 0.74 | 0.62
2 | Calculation surface 2 | Perpendicular illuminance | 93.1 lx | 131 lx | 117 lx | 0.8 | 0.71
3 | Calculation surface 3 | Perpendicular illuminance | 159 lx | 382 lx | 282 lx | 0.56 | 0.42
4 | Calculation surface 4 | Perpendicular illuminance | 200 lx | 375 lx | 305 lx | 0.66 | 0.53
5 | Calculation surface 5 | Perpendicular illuminance | 166 lx | 341 lx | 276 lx | 0.6 | 0.49
6 | Working plane (store 1) | Perpendicular illuminance (Adaptive) | 83.0 lx | 191 lx | 151 lx | 0.55 | 0.43
7 | Working plane (entrance 1) | Perpendicular illuminance (Adaptive) | 42.8 lx | 122 lx | 94.9 lx | 0.45 | 0.35
8 | Working plane (kitchnes) | Perpendicular illuminance (Adaptive) | 233 lx | 661 lx | 522 lx | 0.45 | 0.35
9 | Working plane (patient 1) | Perpendicular illuminance (Adaptive) | 51.2 lx | 150 lx | 111 lx | 0.46 | 0.34
10 | Working plane (clinic 1) | Perpendicular illuminance (Adaptive) | 337 lx | 758 lx | 573 lx | 0.59 | 0.44
11 | Working plane (bathroom1) | Perpendicular illuminance (Adaptive) | 133 lx | 166 lx | 148 lx | 0.9 | 0.8
12 | Working plane (AHU 1) | Perpendicular illuminance (Adaptive) | 119 lx | 333 lx | 244 lx | 0.49 | 0.36
13 | Working plane (clinic 2) | Perpendicular illuminance (Adaptive) | 170 lx | 633 lx | 483 lx | 0.35 | 0.27
14 | Working plane (bathroom2) | Perpendicular illuminance (Adaptive) | 115 lx | 171 lx | 145 lx | 0.79 | 0.67
15 | Working plane (waiting room) | Perpendicular illuminance (Adaptive) | 90.3 lx | 283 lx | 196 lx | 0.46 | 0.32
16 | Working plane (c14) | Perpendicular illuminance (Adaptive) | 54.7 lx | 125 lx | 102 lx | 0.54 | 0.44
17 | Working plane (AHU 2) | Perpendicular illuminance (Adaptive) | 103 lx | 333 lx | 249 lx | 0.41 | 0.31
18 | Working plane (cleaning room) | Perpendicular illuminance (Adaptive) | 109 lx | 235 lx | 180 lx | 0.61 | 0.46
19 | Working plane (dirty room) | Perpendicular illuminance (Adaptive) | 107 lx | 233 lx | 180 lx | 0.59 | 0.46
20 | Working plane (store2) | Perpendicular illuminance (Adaptive) | 72.6 lx | 210 lx | 144 lx | 0.5 | 0.35
21 | Working plane (srairs2) | Perpendicular illuminance (Adaptive) | 112 lx | 137 lx | 126 lx | 0.89 | 0.82
22 | Working plane (c11) | Perpendicular illuminance (Adaptive) | 44.8 lx | 119 lx | 89.7 lx | 0.5 | 0.38
23 | Working plane (leccture hall) | Perpendicular illuminance (Adaptive) | 398 lx | 1762 lx | 1106 lx | 0.36 | 0.23
24 | Working plane (c13) | Perpendicular illuminance (Adaptive) | 55.1 lx | 129 lx | 99.6 lx | 0.55 | 0.43
25 | Working plane (c12) | Perpendicular illuminance (Adaptive) | 53.1 lx | 135 lx | 106 lx | 0.5 | 0.39
26 | Working plane (mulyi-use) | Perpendicular illuminance (Adaptive) | 116 lx | 259 lx | 203 lx | 0.57 | 0.45
27 | Working plane (mulyi-use 2) | Perpendicular illuminance (Adaptive) | 133 lx | 272 lx | 208 lx | 0.64 | 0.49
28 | Working plane (mulyi-use 3) | Perpendicular illuminance (Adaptive) | 156 lx | 297 lx | 233 lx | 0.67 | 0.53
29 | Working plane (stairs1) | Perpendicular illuminance (Adaptive) | 90.7 lx | 134 lx | 120 lx | 0.76 | 0.68
30 | Working plane (dental room) | Perpendicular illuminance (Adaptive) | 290 lx | 706 lx | 546 lx | 0.53 | 0.41
32 | Working plane (bathroom entrance 3) | Perpendicular illuminance (Adaptive) | 73.3 lx | 150 lx | 115 lx | 0.64 | 0.49
33 | Working plane (pharmacy2) | Perpendicular illuminance (Adaptive) | 285 lx | 692 lx | 543 lx | 0.52 | 0.41
34 | Working plane (office1) | Perpendicular illuminance (Adaptive) | 266 lx | 575 lx | 446 lx | 0.6 | 0.46
35 | Working plane (office3) | Perpendicular illuminance (Adaptive) | 266 lx | 577 lx | 443 lx | 0.6 | 0.46
36 | Working plane (ELE ROOM) | Perpendicular illuminance (Adaptive) | 99.9 lx | 268 lx | 205 lx | 0.49 | 0.37
37 | Working plane (bathroom entrance 1) | Perpendicular illuminance (Adaptive) | 200 lx | 380 lx | 313 lx | 0.64 | 0.53
38 | Working plane (c5) | Perpendicular illuminance (Adaptive) | 58.6 lx | 209 lx | 133 lx | 0.44 | 0.28
39 | Working plane (c6) | Perpendicular illuminance (Adaptive) | 46.7 lx | 123 lx | 94.1 lx | 0.5 | 0.38
40 | Working plane (c1) | Perpendicular illuminance (Adaptive) | 51.0 lx | 125 lx | 102 lx | 0.5 | 0.41
41 | Working plane (bathroom2) | Perpendicular illuminance (Adaptive) | 117 lx | 135 lx | 127 lx | 0.92 | 0.87
42 | Working plane (c2) | Perpendicular illuminance (Adaptive) | 51.7 lx | 128 lx | 106 lx | 0.49 | 0.4
43 | Working plane (wating area 5) | Perpendicular illuminance (Adaptive) | 112 lx | 369 lx | 275 lx | 0.41 | 0.3
44 | Working plane (c4) | Perpendicular illuminance (Adaptive) | 53.5 lx | 127 lx | 104 lx | 0.51 | 0.42
45 | Working plane (stairs3) | Perpendicular illuminance (Adaptive) | 105 lx | 132 lx | 122 lx | 0.86 | 0.8
46 | Working plane (bathroom entrance 2) | Perpendicular illuminance (Adaptive) | 47.4 lx | 339 lx | 248 lx | 0.19 | 0.14
47 | Working plane (office2) | Perpendicular illuminance (Adaptive) | 344 lx | 705 lx | 544 lx | 0.63 | 0.49
48 | Working plane (office4) | Perpendicular illuminance (Adaptive) | 312 lx | 611 lx | 499 lx | 0.63 | 0.51
49 | Working plane (entrance 7) | Perpendicular illuminance (Adaptive) | 48.7 lx | 182 lx | 115 lx | 0.42 | 0.27
50 | Working plane (pharmacy3) | Perpendicular illuminance (Adaptive) | 289 lx | 742 lx | 580 lx | 0.5 | 0.39
51 | Working plane (office5) | Perpendicular illuminance (Adaptive) | 316 lx | 628 lx | 486 lx | 0.65 | 0.5
52 | Working plane (patient 2) | Perpendicular illuminance (Adaptive) | 87.1 lx | 154 lx | 124 lx | 0.7 | 0.57
53 | Working plane (ct scan ) | Perpendicular illuminance (Adaptive) | 147 lx | 434 lx | 324 lx | 0.45 | 0.34
54 | Working plane (general 1) | Perpendicular illuminance (Adaptive) | 63.4 lx | 173 lx | 121 lx | 0.52 | 0.37
55 | Working plane (general 2) | Perpendicular illuminance (Adaptive) | 63.2 lx | 173 lx | 121 lx | 0.52 | 0.37
56 | Working plane (store3) | Perpendicular illuminance (Adaptive) | 84.4 lx | 200 lx | 163 lx | 0.52 | 0.42
57 | Working plane (pharmacy1) | Perpendicular illuminance (Adaptive) | 297 lx | 726 lx | 581 lx | 0.51 | 0.41
58 | Working plane (pray area) | Perpendicular illuminance (Adaptive) | 81.5 lx | 197 lx | 160 lx | 0.51 | 0.41
59 | Working plane (blood bank) | Perpendicular illuminance (Adaptive) | 152 lx | 390 lx | 312 lx | 0.49 | 0.39
60 | Working plane (office6) | Perpendicular illuminance (Adaptive) | 295 lx | 602 lx | 470 lx | 0.63 | 0.49
62 | Working plane (bathroom4) | Perpendicular illuminance (Adaptive) | 30.6 lx | 187 lx | 154 lx | 0.2 | 0.16
63 | Working plane (jan) | Perpendicular illuminance (Adaptive) | 108 lx | 132 lx | 121 lx | 0.89 | 0.82
64 | Working plane (dress 1) | Perpendicular illuminance (Adaptive) | 169 lx | 190 lx | 179 lx | 0.94 | 0.89
65 | Working plane (drees 2) | Perpendicular illuminance (Adaptive) | 118 lx | 137 lx | 129 lx | 0.91 | 0.86
66 | Working plane (c16) | Perpendicular illuminance (Adaptive) | 46.3 lx | 144 lx | 104 lx | 0.45 | 0.32
67 | Working plane (bathroom7) | Perpendicular illuminance (Adaptive) | 80.8 lx | 92.4 lx | 87.3 lx | 0.93 | 0.87
68 | Working plane (fluoroscopy x-ray) | Perpendicular illuminance (Adaptive) | 116 lx | 498 lx | 329 lx | 0.35 | 0.23
69 | Working plane (dark room) | Perpendicular illuminance (Adaptive) | 168 lx | 361 lx | 276 lx | 0.61 | 0.47
70 | Working plane (radiologist) | Perpendicular illuminance (Adaptive) | 93.5 lx | 450 lx | 342 lx | 0.27 | 0.21
71 | Working plane (light rooom) | Perpendicular illuminance (Adaptive) | 206 lx | 364 lx | 304 lx | 0.68 | 0.57
72 | Working plane (bathroom6) | Perpendicular illuminance (Adaptive) | 109 lx | 135 lx | 124 lx | 0.88 | 0.81
73 | Working plane (reception 4) | Perpendicular illuminance (Adaptive) | 27.0 lx | 374 lx | 296 lx | 0.091 | 0.072
74 | Working plane (bathroom entrance 4) | Perpendicular illuminance (Adaptive) | 49.7 lx | 179 lx | 112 lx | 0.44 | 0.28
75 | Working plane (bathroom5) | Perpendicular illuminance (Adaptive) | 119 lx | 138 lx | 130 lx | 0.92 | 0.86
76 | Working plane (office7) | Perpendicular illuminance (Adaptive) | 270 lx | 651 lx | 508 lx | 0.53 | 0.41
77 | Working plane (general3) | Perpendicular illuminance (Adaptive) | 77.8 lx | 120 lx | 100 lx | 0.78 | 0.65
78 | Working plane (light lock) | Perpendicular illuminance (Adaptive) | 210 lx | 226 lx | 217 lx | 0.97 | 0.93
79 | Working plane (reception 2) | Perpendicular illuminance (Adaptive) | 168 lx | 448 lx | 385 lx | 0.44 | 0.38
80 | Working plane (reception 3) | Perpendicular illuminance (Adaptive) | 148 lx | 410 lx | 313 lx | 0.47 | 0.36
81 | Working plane (c7) | Perpendicular illuminance (Adaptive) | 52.5 lx | 123 lx | 97.4 lx | 0.54 | 0.43
82 | Working plane (c8) | Perpendicular illuminance (Adaptive) | 74.0 lx | 148 lx | 116 lx | 0.64 | 0.5
83 | Working plane (c10) | Perpendicular illuminance (Adaptive) | 48.1 lx | 120 lx | 94.9 lx | 0.51 | 0.4
84 | Working plane (c9) | Perpendicular illuminance (Adaptive) | 43.5 lx | 144 lx | 100 lx | 0.44 | 0.3
85 | Working plane (reception 1) | Perpendicular illuminance (Adaptive) | 141 lx | 410 lx | 342 lx | 0.41 | 0.34
86 | Working plane (entrance2) | Perpendicular illuminance (Adaptive) | 71.8 lx | 207 lx | 142 lx | 0.51 | 0.35
87 | Working plane (entrance 3) | Perpendicular illuminance (Adaptive) | 41.6 lx | 121 lx | 97.0 lx | 0.43 | 0.34
88 | Working plane (entrance5) | Perpendicular illuminance (Adaptive) | 49.9 lx | 118 lx | 95.2 lx | 0.52 | 0.42
89 | Working plane (wating area4) | Perpendicular illuminance (Adaptive) | 114 lx | 282 lx | 217 lx | 0.53 | 0.4
90 | Working plane (entrance6) | Perpendicular illuminance (Adaptive) | 72.3 lx | 131 lx | 114 lx | 0.63 | 0.55
91 | Working plane (entrance 4) | Perpendicular illuminance (Adaptive) | 79.0 lx | 131 lx | 115 lx | 0.69 | 0.6
92 | Working plane (wating area3) | Perpendicular illuminance (Adaptive) | 151 lx | 280 lx | 224 lx | 0.67 | 0.54
93 | Working plane (wating area1) | Perpendicular illuminance (Adaptive) | 70.9 lx | 128 lx | 111 lx | 0.64 | 0.55
94 | Working plane (wating area2) | Perpendicular illuminance (Adaptive) | 78.5 lx | 129 lx | 114 lx | 0.69 | 0.61
96 | Working plane (c3) | Perpendicular illuminance (Adaptive) | 55.4 lx | 126 lx | 103 lx | 0.54 | 0.44
97 | Working plane (c17) | Perpendicular illuminance (Adaptive) | 78.8 lx | 149 lx | 118 lx | 0.67 | 0.53
98 | Working plane (IT ROOOM) | Perpendicular illuminance (Adaptive) | 102 lx | 233 lx | 187 lx | 0.55 | 0.44